## Slide 1: Fault Tolerant Networking on VOS
Noah Davids
Software Systems Engineer

## Slide 2: Fault Tolerant Networking in General
Routers
Switches
and NICs (network interface cards)
(Oh my!)

## Slide 3: Fault Tolerant Networking Routing
Hardware Fault Tolerance
  Virtual Routers
    Cisco Hot Standby Routing Protocol (HSRP)
    Virtual Routing Redundancy Protocol (VRRP)
      RFC 2338 - Proposed standard
  Dual power supplies
Software Fault Tolerance
  ICMP redirects
  Routing Protocols
    OSPF, RIP
Notes: The idea behind the virtual routers is that they share an IP and MAC address. One router acts as a primary and handles all the routing but if the primary fails the secondary can take over. The hosts using the router see no change. Fail over happens quickly but not instantaneously. Messages in transit will get dropped. Not a problem for TCP but applications using UDP will need a application retransmission algorithm if they care.
All networking devices should have dual power supplies and be connected to independent power sources. A significant source of temporary outages are due to people shutting down a circuit or accidentally pulling a power cord or brushing against a lose power cord.
Using ICMP redirects works only if a link fails and the router can redirect the host to another router on the network with a backup link. If the router itself fails there is nothing to send the redirect. Also once the redirect router is in place recovery back to the primary may not happen until the route times out. Under STCP that will be 10 minutes (if you have STCP-XXX fixed). Other wise the route never times out. Under OS/TCP the route never times out.
If the host can listen to the router protocol that routers use to talk to each other you have a much more dynamic environment. The two common protocols are RIP and OSPF. OS/TCP does not have a mechanism to do this. STCP does support OSPF.

## Slide 4: Fault Tolerant Networking Switching
Hardware Fault Tolerance
  Trunking
    Multiple ports connect 2 switches
  Dual power supplies
Software Fault Tolerant
  Spanning Tree Protocol (STP)
Notes: The idea behind trunking is that you can get more bandwidth between switches. Trunking 5 100mbps ports gives you 500 mbps and less than half the cost of a gigabit link. You get fault tolerance as a freebie, if 1 link fails for some reason the others keep going. You drop in bandwidth but the connection between the two switches stays up. There is also no or at least only a very small amount of recovery time.

## Slide 5: Background – IEEE 802.1D spanning tree algorithm
Spanning tree is a protocol that allows multiple switches to be connected with redundant links but prevents loops by blocking certain ports
  Creates a loop free tree connecting all the switches by blocking redundant links
  Automatically will recover by unblocking a link if a currently active link fails
  Recovery is not instantaneous
    It can take from 5 seconds to 50 seconds or longer to recalculate the loop free tree
    Delays can happen even if there are no redundant links

## Slide 6: Background – IEEE 802.1D spanning tree algorithm
  Recovery may be triggered when a link goes down or comes up
    Recovery can effect switches throughout the network not just the one with the link that changes state
  Some switches may have configuration settings that allow you to adjust or turn off spanning tree
    Cisco’s portfast setting is an example
    You want to do this for ports connected to hosts it will speed up recovery

## Slide 7: Background – IEEE 802.1D spanning tree algorithm
SW2
SW6
SW5
SW4
SW3
SW1
Notes: Green is in forwarding state
Blue is in blocked state

## Slide 8: Background – IEEE 802.1D spanning tree algorithm
SW2
SW6
SW5
SW4
SW3
SW1
Notes: Link between SW3 and SW5 fails. Spanning tree recognizes the change and connects SW5 to SW2. Note that it also changes the connection to SW4, blocking the SW4 to SW5 link and bring up the SW4 to SW2 link. The point is that a single failure can result in several changes in the network.
Green is in forwarding state
Blue is in blocked state
Red is failed

## Slide 9: Fault Tolerant Networking NICs
Multiple NICs on a host all share the same IP address
They may also share the same Ethernet MAC address
Backup can seamlessly take over from a primary in the event that a primary NIC or link fails

## Slide 10: Fault Tolerant Networking NICs (finally something Stratus specific)
VOS OS/TCP
  DLMUX as of VOS 13.2
    K104, K450, K460
VOS STCP
  DLMUX as of VOS 14.1
    K104, K450, K460
  SDLMUX as of VOS 14.2
    U713, U714
Windows 2000
  Intel PROSet (I’m not talking about this)
    U515, U570, U571

## Slide 11: DLMUX OS/TCP Configuration (K104)
/ =name tcp1.6
=module_name m13
=device_type ioa_gdma
=slot 4
=firmware_type hal
=adapter_slot_no 6
=adapter_subchannel_no 0
=parameters '-partner #tcp1.7'
/ =name tcp1.7
=module_name m13
=device_type ioa_gdma
=slot 4
=firmware_type hal
=adapter_slot_no 7
=adapter_subchannel_no 0
=parameters '-partner #tcp1.6'
Notes: What I want to point out is the partner parameter. Notice that each device has a partner pointing to the other.
You can only have 2 NICs in a partnership

## Slide 12: DLMUX STCP Configuration (K104)
/ =name stcp_k104.m13.8.12
=module_name m13
=device_type streams_ioa_gdma
=slot 8
=adapter_slot_no 12
=adapter_subchannel_no 0
=firmware_type hal
=streams_driver ad
=clone_limit 32
=parameters '-partner #stcp_k104.m13.8.13'
/ =name stcp_k104.m13.8.13
=module_name m13
=device_type streams_ioa_gdma
=slot 8
=adapter_slot_no 13
=adapter_subchannel_no 0
=firmware_type hal
=streams_driver ad
=clone_limit 32
=parameters '-partner #stcp_k104.m13.8.12'
Notes: From the perspective of DLMUX the config is the same, I.e. specify the partner in the parameters field.

## Slide 13: DLMUX Drivers
The dlmux driver must be loaded in module_start_up.cm
load_kernel_program >system>kernel_loadable_library>dlmux driver
And it must be loaded before any ifconfig’s are done
The K104, K450, and K460 will not work correctly unless the driver is loaded
  Even if they have no partners

## Slide 14: DLMUX MAC address creation
Each partner has a unique address
The address is based on the NICs role, i.e. active or standby
  When a standby NIC becomes active it takes over the MAC address of the active card which takes on the standby’s address

## Slide 15: DLMUX MAC address creation
Primary (active) interface has a MAC address of
  00:00:A8:8v:wx:yz
Secondary (standby) interface has a MAC address of
  00:00:A8:Av:wx:yz
On Continuum systems
  v index of dl_mux entry
  wx:yz lower 12 bits and bits 14 and 15 of system serial number ORed with 8000x (bit 13 is 0)
On non-Continuum systems
  v index of dl_mux entry
  wx:yz 0ddsssssmmmmmmmm
  dd lower 2 bits of disk_pack UID
  sssss lower 5 bits of system number
  mmmmmmmm lower 8 bits of module number

## Slide 16: DLMUX Fail over rules
if board breaks we fail over immediately
if board reports “carrier loss” we fail over immediately (sort of)
  k104
    may take 10 seconds to recognize lost or reconnect
  k450/k460
    reports carrier lost only when it tries to send something

## Slide 17: DLMUX Fail over rules
dl_mux periodically polls the two interfaces and their network connection
  Poll time is every 45 seconds
  if secondary does not receive poll frame from primary
    listen for broadcast frames
    board that is receiving broadcasts is assumed to be on the network
    if neither card sees broadcasts (or they both do)
      if we have sent a non-test frame out and we haven’t gotten any inbound frames, switch anyway

## Slide 18: DLMUX Fail over rules - recovery
After a failure associated with the physical network interface is resolved (ie. the hardware problem is fixed), DLMUX looks at the status of the I/O and the hardware type.
  K104
    DLMUX will not switch back to the previous interface.
  K450 / K460 (HSC)
    DLMUX will only switch to the restored controller if SCSI is not actively using it. (The change in board states appears in >system>syserr_log.(date))

## Slide 19: DLMUX packet primary to secondary
DLC: ----- DLC Header -----
DLC:
DLC: Frame 2 arrived at 10:31:14.9011; frame size is 60 (003C hex) bytes.
DLC: Destination = Station StrtusAF804A
DLC: Source = Station Strtus8F804A
DLC: 802.3 length = 24
DLC:
LLC: ----- LLC Header -----
LLC:
LLC: DSAP Address = AE, DSAP IG Bit = 01 (Group Address)
LLC: SSAP Address = AE, SSAP CR Bit = 01 (Response)
LLC: Unnumbered frame: Invalid U-type, FINAL
LLC:
LLC: ERROR: Data is not allowed for this format
DLC: Frame padding= 22 bytes
ADDR HEX ASCII
0000 00 00 A8 AF 80 4A 00 00 A8 8F 80 4A 00 18 AF AF .....J.....J....
0010 F7 31 32 39 2E 31 2E 30 D7 F4 C6 73 2C 32 FF FF .129.1.0...s,2..
0020 FF FF 04 07 00 A1 00 3F 7A A9 30 35 02 01 00 04 .......?z.05....
0030 06 70 75 62 6C 69 63 A1 28 02 04 36 .public.(..6
Notes: Note the invalid U-type and error “Data is not allowed for this format”. Don’t worry about them the frame doesn’t conform to the LLC standard but since we are not trying to talk with anyone else it doesn’t really matter.

## Slide 20: DLMUX packet secondary to primary
DLC: ----- DLC Header -----
DLC:
DLC: Frame 3 arrived at 10:31:14.9012; frame size is 60 (003C hex) bytes.
DLC: Destination = Station Strtus8F804A
DLC: Source = Station StrtusAF804A
DLC: 802.3 length = 24
DLC:
LLC: ----- LLC Header -----
LLC:
LLC: DSAP Address = AE, DSAP IG Bit = 01 (Group Address)
LLC: SSAP Address = AE, SSAP CR Bit = 01 (Response)
LLC: Unnumbered frame: Invalid U-type, FINAL
LLC:
LLC: ERROR: Data is not allowed for this format
DLC: Frame padding= 22 bytes
ADDR HEX ASCII
0000 00 00 A8 8F 80 4A 00 00 A8 AF 80 4A 00 18 AF AF .....J.....J....
0010 F7 31 32 39 2E 31 2E 30 00 4B 16 DE C6 73 2C D6 .129.1.0.K...s,.
0020 FF FF FF FF FF FF C6 73 2C 2B 01 00 00 00 01 C6 .......s,+......
0030 73 2C D6 00 00 00 00 00 00 00 00 00 s,..........

## Slide 21: DLMUX syserr_log messages
12:15:02 dlmux_timers.c: 951: dlmux_generate_rsn_call: Device %phx_cac_j14#enet
+.14.4 not responding to DLMUX testing
Generated no more than once per day per adapter
Failure count >= 10
  Failure count incremented every time test message fails
  Failure count decremented every time test message succeeds
    will not go below 0

## Slide 22: DLMUX syserr_log mesages
12:06:47 dlmux: switching from %phx_cac_j14#enet.14.5 to %phx_cac_j14#enet.14.4
+ due to packet loss
issued when dlmux changes the active interface because of a test message failure

## Slide 23: DLMUX syserr_log messages
10:59:17 dlmux: switching from %phx_cac_j14#enet.14.4 to %phx_cac_j14#enet.14.5
+ for BIO/SCSI load balancing
Issued when dlmux moves the active interface off of the adapter that is handling the SCSI disks
  (only for K450/K460s)

## Slide 24: DLMUX syserr_log messages
11:41:00 dlmux: switching from %phx_cac_j14#enet.14.5 to %phx_cac_j14#enet.14.4
+ by operator request
11:41:01 Noah_Davids.CAC on terminal telnet_m14.3: dlmux_admin: Device Name=%ph
+x_cac_j14#enet.14.5;Action=failover
Issued when a manual failover is done via dlmux_admin command

## Slide 25: DLMUX tuning variables
dlmux_default_mac_addr$
  sets a value to by-pass the continuum serial number or the non-continuum disk_pack/system/module combination
    note only lower 16 bits are used, the 00:00:A8:Av bytes are calculated per the previous slide

## Slide 26: DLMUX netstat
netstat –detail (OS/TCP) or netstat –interface (STCP) provides information ONLY about the active adapter.
  Statistics are reset when the adapter becomes active
You cannot get any information about the inactive adapter from netstat

## Slide 27: DLMUX analyze_system requests
as: dump_dlmux_info
client_entry_ptr[0] FEB63488
adapter lockp[0] C0929340
. . .
dlmux adapter entry @0xFEB633A4
name: %phx_cac_j14#enet.14.4
device id: 0405FFFF
state: test open
flags: partner asgnd user_sel
adapter_index: 0
client_index: 0
adapter_type: 58
mac_addr: 0000A8A081DE
dvtep: C0CF41C0
fail_count: 0
state_change_callback : tcp_dlm_utils+7D0, line 367 (FEAB1F10)
free_buf_call : bufman+13A0, line 1386 (FEA9ADA0)
get_buf_call : tcp_dlm_utils+488, line 195 (FEAB1BC8)
put_buf_up_call : tcp_dlm_utils+10E0, line 794 (FEAB2820)
put_attr_up_call : tcp_dlm_utils+13D8, line 926 (FEAB2B18)
relax_flow_call : [none]

## Slide 28: dlmux_admin command
dlmux_admin #enet.14.5 failover
ready 11:54:05
dlmux_admin #enet.14.4 get_status
Device Name: %phx_cac_j14#enet.14.4
Adapter State: ACTIVE UP
Partner: %phx_cac_j14#enet.14.5
Partner State: UP
ready 11:54:22
as: match 'name:' -or 'flags:'; dump_dlmux_info
name: %phx_cac_j14#enet.14.4
flags: asgnd user_sel
name: %phx_cac_j14#enet.14.5
flags: partner asgnd user_sel
as: q
dlmux_admin #enet.14.4 allow_bio_scsi_load_balancing
ready 11:56:18
as: match 'name:' -or 'flags:'; dump_dlmux_info
name: %phx_cac_j14#enet.14.4
flags: partner asgnd
name: %phx_cac_j14#enet.14.5
flags: asgnd
Notes: I am going to go over some of the more important dlmux_admin actions – not all of them
First get_status – tells you which interface is active and which is standby
The failover action lets you change this, lets say you are going to upgrade the switch that 14.5 is connected to so you failover 14.5 making 14.4 active.
The problem is that once you do this the system will stop trying to load balance SCSI and Ethernet on different adapters. The User has selected (note the user_sel flag in dump_dlmux_info) the adapter.
Once the switch is upgraded you fail failover again but the user_sel flag is still set so if for some reason the scsi switches you are back to both one 1 card.
The “allow_bio_scsi_load_balancing” action clears the user_sel flags.

## Slide 29: dlmux_admin command
as: match 'name:' -or 'count:'; dump_dlmux_info
name: %phx_cac_j14#enet.14.4
fail_count: 1875
name: %phx_cac_j14#enet.14.5
fail_count: 1
as: q
ready 12:23:28
dlmux_admin #enet.14.4 clear_counts
ready 12:24:03
dlmux_admin #enet.14.5 clear_counts
ready 12:24:10
as: match 'name:' -or 'count:'; dump_dlmux_info
name: %phx_cac_j14#enet.14.4
fail_count: 0
name: %phx_cac_j14#enet.14.5
fail_count: 0
as: q
ready 12:24:13
Notes: Lets say that one of your switches has been down for 2 weeks. Every day you have been getting a
dlmux_timers.c: 951: dlmux_generate_rsn_call: Device %phx_cac_j14#enet
+.14.4 not responding to DLMUX testing
Message. Things are now working and you expect the messages to stop – and they will – in 2 weeks. The counter goes down just as fast as it went up.
To clear the problem you can use the dlmux action clear_counts. Note that you have to clear each adapter separately, unlike the allow_bio_scsi_load_balancing which cleared the flag on both partners.

## Slide 31: SDLMUX Configuration
/ =name stcp_u713.m13.8.3
=module_name m13
=device_type streams_pci
=streams_driver renet
=slot 8
=adapter_slot_no 3
=adapter_subchannel_no 0
=clone_limit 32
=parameters '-partner #stcp_u713.m13.9.3 -sdlmux #sdlmux3'
/ =name stcp_u713.m13.9.3
=module_name m13
=device_type streams_pci
=streams_driver renet
=slot 9
=adapter_slot_no 3
=adapter_subchannel_no 0
=clone_limit 32
=parameters '-partner #stcp_u713.m13.8.3 -sdlmux #sdlmux3'
Notes: Note that not only do the parameters in each device point to the other device but both of the devices refer to the same sdlmux device – which must also be defined.
Each partnership must refer to its own sdlmux device. Devices names can be anything but I suggest that they relate back to the K470 slot that the actual cards are in.

## Slide 32: SDLMUX Configuration
/ =name sdlmux3
=module_name m13
=device_type streams
=streams_driver sdlmux
=clone_limit 32

## Slide 33: SDLMUX Configuration
Stratus recommends that all U714 and U713 cards be configured with sdlmux – even if they are not configured with a partner.
  Without sdlmux if a card is broken and comes back into service any multicast addresses that are being listened to are lost.

## Slide 34: SDLMUX Drivers
sdlmux dynamically loads when sdlmux is init’ed
dlmux_admin #u713.m14.6.3 init_sdlmux
This is done in the start_stcp command macro
  This must be done for every device pair using sdlmux
Notes: You only need to do the init_sdlmux for 1 of the devices in a pair
Ifconfig refers to the sdlmux device not the actual adapter device names.

## Slide 35: SDLMUX MAC address creation
Primary (active) interfaced has a MAC address of
  00:00:A8:Cv:wx:yz
Secondary (standby) interface has a MAC address of
  00:00:A8:Ev:wx:yz
  v index of sdlmux entry
  wx:yz lower 12 bits and bits 14 and 15 of
  system serial number ORed with
  8000x (bit 13 is 0)
Notes: The burned in MAC address of the Ethernet Chip is never used.

## Slide 36: SDLMUX Fail over rules
if board breaks we fail over immediately
if board reports that carrier was lost we fail over immediately

## Slide 37: SDLMUX Fail over rules
sdlmux periodically polls the two interfaces and their network connection
  poll time pattern
    5 tests, once every 3 seconds followed by a 57 second pause
Fail over will occur if
  primary does not receive poll frames and is NOT receiving normal data frames
  primary receives poll frame but secondary does NOT
fail over will NOT occur if
  primary does not receive poll frames but is receiving normal data frames
  Neither primary nor secondary receive poll frames but primary is receiving normal data frames

## Slide 38: SDLMUX Fail over rules - recovery
After a failure associated with the physical network interface is resolved (i.e. the hardware problem is fixed), SDLMUX will take no special action other than to note that the standby card is now working correctly, I.e. can be come active if necessary.

## Slide 39: SDLMUX packet primary to secondary
DLC: ----- DLC Header -----
DLC:
DLC: Frame 3 arrived at 12:57:07.4499; frame size is 60 (003C hex) bytes.
DLC: Destination = Station StrtusE081DE
DLC: Source = Station StrtusC081DE
DLC: 802.3 length = 10
DLC:
LLC: ----- LLC Header -----
LLC:
LLC: DSAP Address = AC, DSAP IG Bit = 00 (Individual Address)
LLC: SSAP Address = AC, SSAP CR Bit = 00 (Command)
LLC: Unnumbered frame: UI
LLC:
???: ----- SAP data -----
???:
???: [7 bytes of information]
???:
DLC: Frame padding= 36 bytes
ADDR HEX ASCII
0000 00 00 A8 E0 81 DE 00 00 A8 C0 81 DE 00 0A AC AC ................
0010 03 31 32 39 2E 31 2E 30 00 00 00 00 00 00 00 00 .129.1.0........
0020 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 ................
0030 00 00 00 00 00 00 00 00 00 00 00 00 ............

## Slide 40: SDLMUX packet secondary to primary
DLC: ----- DLC Header -----
DLC:
DLC: Frame 4 arrived at 12:57:07.4500; frame size is 60 (003C hex) bytes.
DLC: Destination = Station StrtusC081DE
DLC: Source = Station StrtusE081DE
DLC: 802.3 length = 10
DLC:
LLC: ----- LLC Header -----
LLC:
LLC: DSAP Address = AC, DSAP IG Bit = 00 (Individual Address)
LLC: SSAP Address = AC, SSAP CR Bit = 00 (Command)
LLC: Unnumbered frame: UI
LLC:
???: ----- SAP data -----
???:
???: [7 bytes of information]
???:
DLC: Frame padding= 36 bytes
ADDR HEX ASCII
0000 00 00 A8 C0 81 DE 00 00 A8 E0 81 DE 00 0A AC AC ................
0010 03 31 32 39 2E 31 2E 30 00 00 00 00 00 00 00 00 .129.1.0........
0020 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 ................
0030 00 00 00 00 00 00 00 00 00 00 00 00 ............

## Slide 41: SDLMUX syserr_log mesages
15:24:23 WARNING(33): SDLMUX: switching from %phx_cac_j14#stcp_u713.m14.6.1 t
+o %phx_cac_j14#stcp_u713.m14.7.1 in group #sdlmux1 due to packet loss
issued when sdlmux changes the active interface because of a test message failure

## Slide 42: SDLMUX syserr_log messages
14:09:29 WARNING(29): SDLMUX: switching from %phx_cac_j14#stcp_u713.m14.6.1 t
+o %phx_cac_j14#stcp_u713.m14.7.1 in group #sdlmux1 by operator request
14:09:29 Noah_Davids.CAC on terminal telnet_m14.3: dlmux_admin: Device Name=%p
+hx_cac_j14#stcp_u713.m14.6.1;Action=failover
Issued when a manual failover is done via dlmux_admin command

## Slide 43: SDLMUX syserr_log messages
15:23:05 WARNING(30): renet (7/1): Network cable lost.
15:23:05 WARNING(31): SDLMUX: switching from %phx_cac_j14#stcp_u713.m14.7.1 t
+o %phx_cac_j14#stcp_u713.m14.6.1 in group #sdlmux1 due to link loss
Issued when active adapter has a link loss.

## Slide 44: SDLMUX tuning variables
There are no tuning parameters for sdlmux.

## Slide 45: SDLMUX netstat
netstat –interface #SDLMUX_DEV
  Provides the standard set of Ethernet statistics for both the active and standby adapters
    Active adapter is first
    It also provides a count of the number of failovers
    Fail overs do not reset the statistics

## Slide 46: SDLMUX netstat
netstat –interface #device
  You can also do a netstat on just a single device, even if it is part of an sdlmux partnership
    You get just the link layer statistics

## Slide 47: SDLMUX analyze_system requests
dump_sdlmux
  Doesn’t show anything that most people would find useful.
  netstat will give you the same information.

## Slide 48: dlmux_admin command
dlmux_admin #stcp_u713.m14.6.1 init_sdlmux
The init_sdlmux action causes the sdlmux driver to be loaded if it is not already loaded
Both partners are initialized under sdlmux
The interface identified by the sldmux parameter is initialized

## Slide 49: dlmux_admin command
dlmux_admin #stcp_u713.m14.6.1 uninit_sdlmux
The uninit_sdlmux action causes the reverse of the init_sdlmux action
You cannot do this until the sdlmux interface has been deleted via ifconfig -delete

## Slide 50: dlmux_admin command
dlmux_admin #sdlmux1 sdlmux_status
Group Name: #sdlmux1
Device Name: %phx_cac_j14#stcp_u713.m14.7.1
Adapter State: ACTIVE UP
Partner: %phx_cac_j14#stcp_u713.m14.6.1
Partner State: UP
Displays the status of the adapters in the sdlmux group

## Slide 51: dlmux_admin command
dlmux_admin #stcp_u713.m14.7.1 get_status
Group Name: #sdlmux1
Device Name: %phx_cac_j14#stcp_u713.m14.7.1
Adapter State: ACTIVE UP
Partner: %phx_cac_j14#stcp_u713.m14.6.1
Partner State: UP
Displays the status of the adapters and the sdlmux group name

## Slide 52: Gotcha’s
Spanning tree timers
  Even if DLMUX/SDLMUX fails over within seconds, it doesn’t help if spanning tree has blocked ports while it calculates a loop free tree. This can greatly increase the time for a complete fail over
    Turn off spanning tree on the ports connected to the NICs

## Slide 53: Gotcha’s (background) switch address cache
Every switch has an address cache that matches an Ethernet MAC address to a port
It populates the cache by watching what MAC source addresses are arriving at the ports

## Slide 54: Gotcha’s switch address cache
SW2
SW6
SW5
SW4
SW3
SW1
Stratus
Client
sra
sra
sra
sra
sra
Notes: sra indicates, from the switches perspective the outgoing port for the Stratus server

## Slide 55: Gotcha’s switch address cache
SW2
SW6
SW5
SW4
SW3
SW1
Stratus
Client
sra
sra
sra
sra
Notes: Until the Stratus sends out a packet SW4 doesn’t realize that there has been a change so will not forward any packets to the Stratus.
Even through SW5 knows that the Stratus is no longer connected and floods a message to the Stratus to all ports including SW4, SW4 doesn’t know until the Stratus actually sends something so it will not forward the message to the Stratus

## Slide 56: Gotcha’s switch address cache
SW2
SW6
SW5
SW4
SW3
SW1
Stratus
Client
sra
sra
sra
sra
sra
Notes: sra indicates, from the switches perspective the outgoing port for the Stratus server

## Slide 57: Gotcha’s switch address cache
SW2
SW6
SW5
SW4
SW3
SW1
Stratus
Client
sra
sra
sra
sra
sra
Notes: Until the address caches are updated the Stratus packets from the client go to the wrong switches

## Slide 58: Gotcha’s
Switch security settings
  Some switches can be set to allow only a specific MAC address to connect to a port. This kind of setting will not work because the MAC address can change depending on whether the port is acting as the active or standby

## Slide 59: Gotcha’s
Filtering non-IP traffic
  Switches that are set to filter traffic may inadvertently filter the test messages which are not IP traffic. Switches must allow these messages through.

## Slide 60: References
Using HSRP for fault-tolerant IP Routing
  http://www.cisco.com/univercd/cc/td/doc/cisintwk/ics/cs009.htm
Virtual Router Redundancy Protocol (vrrp)
  http://www.ietf.org/html.charters/vrrp-charter.html
  http://www.ietf.org/rfc/rfc2338.txt

## Slide 61: References
Understanding Spanning-Tree Protocol
  http://www.cisco.com/univercd/cc/td/doc/product/rtrmgmt/sw_ntman/cwsimain/cwsi2/cwsiug2/vlan2/stpapp.htm